[image: image6.png]Reliable Clean Power for Everyone



[image: image8.png]Reliable Clean Power for Everyone



                                                                                                        [image: image9.png]Xi’an JDEnergy CO., LTD

25# Bi Yuan 1* Road, High-Tech District of Xi’an,
Shaanxi, China



                
[image: image7.png]Xi’an JDEnergy CO., LTD

25# Bi Yuan 1* Road, High-Tech District of Xi’an,
Shaanxi, China



[image: image10.png]


                                                                                                     [image: image7.png]                

 意大利AFORE ITALIA S.R.L.有限公司
15台欧版eBlock-100C储能项目
   AFORE ITALIA S.R.L.  . 

15 sets European standard eBlock-100C Energy Storage Project 

[image: image8.png]
技术协议
Technical Agreement

Between

买方：意大利AFORE ITALIA S.R.L.有限公司
Buyer: AFORE ITALIA S.R.L.   .

And
卖方：奇点能源（香港）有限公司
Seller: JD ENERGY (HONG KONG) LIMITED.
签订日期：                                   ，Date of signing:                                   .
Content
5

1. Overview 概述

5

1.1. Rights and Obligations of Buyer买方的权利和义务

7

1.2.Rights and Obligations of Seller卖方的权利和义务

7

1.3.Storage Requirements存储要求

9

2.Comply the Standard符合标准

10

3.System Design 系统设计

10

3.1 System Equipment List (Supply Scope) 系统设备清单(供货范围)

12

4. Intelligent Energy Block eBlock-100C 智慧能量块eBlock-100C

12

4.1 General 通用

12

4.1.1 eBlock-100C Liquid Cooling 液冷

12

4.1.2 Product Specification产品规格

14

4.2 Lithium-ion Battery 锂离子电池

14

4.2.1 Battery cell 电池单体

15

4.2.2 Battery pack 电池PACK

15

4.2.3 Battery Rack 电池簇

16

4.3 Battery Management System 电池管理系统

16

4.3.1 BMS Functionality  BMS 功能

17

4.4 Power Conversion System 储能变流器

17

4.4.1 Topology Diagram 拓扑图

18

4.4.2 Product Specification 产品规格

20

4.5 Auxiliary Equipment 辅助设备

20

4.5.1 Liquid Cooling System 液冷系统

21

4.5.2Fire Suppression System  消防系统

22

5.Technical Documents and Drawings技术文件和图纸

22

5.1.General Requirements一般要求

22

5.2. Required Technical Documents and Drawings 要求的文件及图纸

23

5.3.Documents and Drawings to be Provided with the Shipment随运提供的文件和图纸

24

6.Miscellaneous其它事项




Abbreviations 缩写
	JD Energy
	Xi’an JDEnergy Co., Ltd奇点能源股份有限公司

	AHJ
	Authorities Having Jurisdiction 有管辖权的当局

	BESS
	Battery Energy Storage System 电池储能系统

	BMS
	Battery Management System 电池管理系统

	BMU
	Battery Management Unit 电池管理组

	BCS
	Block Control System 能量块控制系统

	EMS
	Energy Management System 能量管理系统

	BOL
	Beginning of Life起始寿命

	ETH
	Ethernet Module以太网模块

	TMS
	Thermal management system热管理系统

	CAN
	Controller Area Network控制器区域网络

	DOD
	Depth of Discharge 放电深度

	FSS
	Fire Suppression System灭火系统组件

	PCS
	Power Conversion System 储能变流器

	SOC
	State of Charge 荷电状态

	SOE
	State of Energy电池电量状态

	SOP
	State of Power功率状态

	SOH
	State of Health 电池健康度

	POI 
	Point of Interconnection 互连点


1. Overview 概述
The purpose of this document is to define the supply scope of Seller for Battery Energy Storage System (BESS) projects and clarify the technical features of all equipment within the supply scope.

本文件旨在明确卖方对电池储能系统(BESS)项目的供货范围，明确供货范围内所有设备的技术特点。
In order to avoid any misunderstanding, matters not mentioned in this part should be determined by the parties to the contract through negotiation during the contract negotiation.
为避免任何误解，本部分未尽事宜，由合同签约双方在合同谈判时协商确定。
The seller guarantee to provide high-quality products and corresponding services that meet the requirements of industrial standards and this Technical Agreement, have complete functions and excellent performance, and meet mandatory national standards and specifications related to safety and environmental protection. 

卖方保证提供符合工业标准和本技术协议书要求并且功能完整、性能优良的优质产品及其相应服务，同时满足与安全、环保等相关的强制性标准和规范。
Buyer understands and agrees that they are responsible for ensuring that the products which they have purchased from Seller meet the requirements of the applicable authorities having jurisdiction (“AHJ”) over the project. Seller takes no responsibility for ensuring that the products meet any AHJ requirements which are currently in effect, or which may be adopted by an AHJ in the future. 

买方理解并同意，买方负责确保其从卖方购买的产品符合对项目有管辖权的当局(“AHJ”)的相关适用要求。卖方不负责确保产品符合AHJ目前有效的或未来可能被AHJ采用的任何要求。
Rights and Obligations of Buyer买方的权利和义务
1) Buyer shall ensure the safety of the Products provided and delivered by Seller,including taking corresponding measures against flood,fire,theft,pests,and sand/dust heavy environment. Without Seller prior written consent,Buyer shall never dissect or dismantle,dissemble or reverse-engineer any Product in whole or in part.
买方应确保卖方提供和交付的产品安全，包括采取应对洪水、火灾、盗窃、虫害和沙尘等环境的相应措施。未经卖方事先书面同意，买方不得对任何产品的全部或部分进行解剖、拆卸、拆解或改造。
2)Buyer shall promptly inform the personnel of Seller in case any abnormality is observed on the Product provided by Seller .Seller personnel shall present on site or support remotely to check the status of Product.
如果发现卖方提供的产品出现异常，买方应立即通知卖方人员。卖方人员应在现场或远程支持，以检查产品的状态。
3)Buyer shall ensure that the BESS will not run in any severe environment with high temperature,high heat,radiation,impact or immersion.
买方应确保BESS不会在任何高温、高热、辐射、冲击或浸泡的恶劣环境中运行。
Seller provides training and support to Buyer .
卖方为买方提供培训和支持。
5) Buyer shall be responsible for the unloading of delivered BESS, provide a site for the storage of BESS and have them in its custody.In addition.Buyer shall protect the delivered BESS from damage, loss, deformation, dampness and corrosion.
买方应负责卸载交付的BESS，为BESS提供储存场所，并将其保管。此外买方应保护交付的BESS免受损坏、丢失、变形、潮湿和腐蚀。
6)Buyer shall assist the personnel of Seller on site,provide or assist with required accommodation, sustenance, transportation and communication, and the access rights to this project to provide technical support for installation and commission. Where the Product of Seller is delivered to the place specified by Buyer,Buyer shall be responsible for the custody of the Product after delivery, Seller shall not be responsible for any loss or damage attributable to Buyer.
买方应在现场协助卖方人员，提供或协助提供所需的住宿、食物、运输和通信，以及进入项目现场的许可。当卖方的产品交付到买方指定的地点后，买方负责对产品进行保管。卖方不对买方造成的任何损失或损害负责。
7)Buyer shall not carry out and be solely responsible for any operation related to overcharging, over-discharging, abuse, short-circuiting that may cause damage to the ESS.
买方不得进行任何与过度充电、过度放电、滥用、短路有关的操作，这些测试可能会对储能系统造成损坏，如有违反，买方将承担全部责任。

Buyer shall be responsible to provide  the auxiliary power 400Vac 50/60Hz for this BESS project on project site.
买方需在该项目现场为此储能项目提供400V 50/60Hz辅助电源。
1.2.Rights and Obligations of Seller卖方的权利和义务
1)Seller shall provide Buyer with reliable Products, commissioning and related technical support confirmed by both parties.
卖方应向买方提供可靠的产品，以及双方确认的调试和相关技术支持。
2)The Products provided by Seller to Buyer shall meet the parameter requirements stipulated in this Agreement.
卖方向买方提供的产品应符合本协议规定的参数要求。
3)Seller shall provide the necessary technical services for the Product.The technical service shall contain technical support of installation ,commission and training.
卖方应为产品提供必要的技术服务。服务包括安装、调试技术支持及培训。
4)After the technical specification is mutually agreed, Seller shall not make any change to the technical specification without the written consent of Buyer.For any change in the design parameters or other important technical parameters , Seller shall inform Buyer in advance and obtain the prior written consent of Buyer.
双方同意技术规范后，未经买方书面同意，卖方不得对技术规范进行任何更改。对于设计参数或其他重要技术参数的任何变更，卖方应提前通知买方，并事先获得买方的书面同意。
5)Seller shall provide the information related to its Product at the reasonable request of Buyer.

卖方应在买方的合理要求下提供与其产品相关的信息。
1.3.Storage Requirements存储要求
Buyer shall ensure that the BESS is stored in environment  where the average temperature<25℃,humidity<95%.If there is a conflict of   storage environment temperature range requirement between the warranty   agreement and this agreement,the warranty agreement shall prevail.However it will accelerate the degradation of BESS capacity if the storage condition ≥25℃.

买方应确保BESS储存在平均温度<25℃、湿度<95%的环境中。如果保修协议与本协议的存储环境温度范围要求不一致，以保修协议为准。但是，如果储存条件≥25℃，将会加速储能系统容量的衰减。
2)If the period between shipment date from factory of Seller and the completion date of  installation & commission exceeds 3 months,the capacity of BESS shall be reduced .In this case,the initial degradation corresponds to the irreversible degradation reflecting the period, So the device should be operated as soon as possible within 3 months after the shipment from factory of Seller .
如果工厂发货日期和现场安装调试日期之间的时间超过3个月，储能系统容量将会减少。在这种情况下，初始衰减为不可逆衰减，所以储能系统应该在工厂发货后三个月内尽快运行设备。

2.Comply the Standard符合标准
	国家

Country
	规范

Regulation
	标准

Standard
	备注

Marks

	Italy
	Safety for eBlock
	EN 62477-1

IEC 62477-1

IEC 62109
	Safety Regulation for PCS and ESS

	
	EMC
	EN IEC 61000-6-1
	EMC 

	
	
	EN IEC 61000-6-2
	

	
	
	EN IEC 61000-6-3
	

	
	
	EN IEC 61000-6-4:
	

	
	
	EN 62920:2017
	

	
	
	
	

	
	Grid code 
	CEI 0-21
	Italian Grid Code

	
	Safety for Batteries
	IEC 62619
	Safety Regulation for Battery

	
	
	IEC 63056
	

	
	
	IEC 60730-1 ANNEX H
	

	
	eBlock
	UN38.3
	


3.System Design 系统设计

3.1 System Equipment List (Supply Scope) 系统设备清单(供货范围)

系统设备清单
 System Equipment List
	No. 

序号
	Item 

设备项
	Specification 

型号
	Qty

数量 
	Unit 

单元
	Remark 

备注

	1
	Intelligent
Energy Block

智慧能量块
	eBlock-100C
	15
	pcs 
	-Each Block consists of 1.1 ~1.5. 

-Using a 3.2V 314Ah LFP battery cell.
-Continuous discharge rate ≤0.5P.
-Nameplate Capacity is 120kWh.
-Dimension（W*D*H）：1000mm×1000mm×2270mm
-Composed of 1 battery rack 1P128S.
-Each battery Rack consists of 4 battery Packs.
-每个Block 由 1.1 ~1.5组成。
-采用3.2V 314Ah磷酸铁锂电芯。
-持续放电倍率≤0.5P。
-铭牌容量为120kWh。
-（W*D*H）：1000mm×1000mm×2270mm
-由1个电池簇组成，组成方式1P128S。
-每个电池簇由4个电池组组成。

	1.1
	PCS

储能变流器
	JS050FA
	15
	pcs 
	-PV Input Max Power (Single Cabinet):100kW
-AC Rated Power (Single Cabinet):50kW
-AC Output: 400V,50Hz

-Phase Configuration: Three-phase, four-wire.

-Cooling System: Integrated liquid cooling system

-光伏输入最大功率（单台）：100kW。
-交流额定功率：50kW。
-交流输出400V，50Hz。

-接线方式：三相四线
-冷却系统：液冷系统。

	1.2
	Battery Pack

电池PACK
	JK31F132H
	60
	pcs 
	- Each eBlock consists of 4 battery packs 
- 每个eBlock由4个电池PACK组成。

	1.3
	BCS Control Software

电池管理系统控制软件
	Battery management  and control system software v1.0
	15
	pcs 
	

	1.4
	Thermal Management System

热管理系统
	Liquid cooling
	15
	pcs 
	Rated refrigeration power 3.5kW.
- 额定制冷功率3.5kW。

	1.5
	柜体及附件

Cabinet body and accessories
	
	15
	pcs
	

	2
	底座

Foundation
	
	15
	pcs
	eBlock - 100C steel structure base plate
- eBlock-100C 配套钢结构底座

	3
	EMS
	eMind
	1
	set
	- Cloud deployment includes Web side and APP
-云端部署包括网页端及APP端

	4
	汇流控制柜

Combiner control cabinet
	eLink-100-4H
	4
	pcs 
	-eBlock-100C is used when multiple parallel machines are On/off grid used, and the maximum support is 4 parallel machines

-eBlock-100C多台并/离网时使用，最大支持4台并机


NOTES: 
The cable from eBlock to the buyer's distribution box is not included and shall be provided by the buyer.

The seller will provide the electricity meter but not the CT. The buyer needs to prepare it by themselves.

注:
不包含eBlock至买方配电箱的电缆，由买方提供。
卖方提供电表，但不提供CT，需买方自备。

4. Intelligent Energy Block eBlock-100C 智慧能量块eBlock-100C
4.1 General 通用
4.1.1 eBlock-100C Liquid Cooling 液冷
[image: image1.png]



Appearance diagram of eBlock-100C (Reference only)
eBlock-100C 外观图(仅供参考)

4.1.2 Product Specification产品规格
Technical Parameters of eBlock-100C 
eBlock-100C技术参数
	Type Designation
类型名称
	eBlock-100C

	光伏参数PV Data

	最大光伏输入功率
Maximum PV Input Power
	100kWp

	最大直流输入电压
Maximum DC Input Voltage
	1000V

	额定直流母线电压
Rated DC Bus Bar Voltage
	720V

	MPPT电压范围
MPPT Voltage Range
	150-900V

	光伏侧特性
PV Function
	可分断直流开关
DC switch

	电池参数Battery Data

	整机额定容量
Rated Capacity
	120kWh

	DOD
	100%

	电网输入侧参数Grid Input Data

	电网额定电压
Rated Voltage
	400V（-15%~10%）3L/N/PE

	最大输入功率
Maximum Input Power
	100kVA

	电网输入频率
Rated Frequency
	50Hz

	电网最大输入电流
Maximum Input Current
	144A

	并网侧参数On grid Data

	额定输出功率
Rate Output Power
	50kW

	最大输出功率
Maximum Output Power
	55kVA/long-term；

	功率因数

Power Factor
	-0.8~0.8

	额定输出线电压
Rated Output Voltage
	400V（-15%~10%）3L/N/PE

	设备外壳体颜色

Equipment enclosure color
	RAL9003

	设备外壳体丝印

Equipment enclosure logo
	Yes/ No
If yes, the requirement provided by customer 

如果是，丝印要求由客户提供


4.2 Lithium-ion Battery 锂离子电池
4.2.1 Battery cell 电池单体

Specification of Battery cell
电池单体规格

	Sample 示样图
	Item 项
	Specification 参数

	[image: image2.jpg]



(For reference only)
	Type of Battery

电池类型
	LFP 314Ah

	
	Nominal voltage

标称电压
	3.2V

	
	Nominal Capacity
标称能量
	1004.8Wh

	
	Nominal voltage

额定电压
	3.2V

	
	Nominal charge/discharge rate

标称充/放电倍率
	≤0.5P

	
	Internal resistance

内阻
	0.18±0.05mΩ

Fresh cell （~30%SOC）

	
	Number of cycles

循环次数
	7000

	
	Operation temperature

工作温度
	0~60℃ Charging
-20~60℃ Discharging

	
	Storage temperature

储存温度
	-35~60℃

Storage ambient humidity < 85% ROH, no condensation

	
	Dimension (W×H×D) (mm)

尺寸
	174.26±0.8*204.44±0.8*71.55±0.8

	
	Weight (kg)

重量
	5.49kg±0.3kg


4.2.2 Battery pack 电池PACK
Specification of Battery Pack
电池PACK规格

	Sample 示样图
	Item 项目
	Specification 参数

	[image: image3.png]



(For reference only)
	Type of Battery 电池类型
	LFP 314Ah

	
	Configuration  配置
	1P32S

	
	Nominal Capacity标称容量
	32.15kWh

	
	Nominal Voltage 标称电压
	DC 102.4V

	
	Operating Voltage工作电压
	89.6~115.2V


4.2.3 Battery Rack 电池簇
The battery Rack adopts a frame structure, and the battery Pack is fixed by bolts.
The battery Rack consists of 4 battery Packs. The battery Packs are arranged in the energy storage cabinet from bottom to top and connected through dedicated connectors on the front panel. The nominal voltage is 409.6V.
电池簇采用框架式结构，电池Pack通过螺栓固定。

电池簇包括4个电池Pack，电池Pack从下到上依次布置于储能柜，通过前面板的专用连接器连接。标称电压为409.6V。
Specification of Battery Rack
电池簇规格

	Sample
	Item 项
	Specification

参数

	[image: image4.png]



(For reference only)
	Type of Battery 电池类型
	LFP 314Ah

	
	Configuration  配置
	1P128S

	
	Key Components 关键部件
	4 Packs

	
	Nominal Capacity 标称容量
	120kWh

	
	Nominal Charge/Discharge Rate

标称充/放电倍率
	≤0.5P

	
	Nominal Voltage 

标称电压
	DC 409.6V

	
	Operating Voltage Range 

工作电压范围
	358.4~460.8V


4.3 Battery Management System 电池管理系统
4.3.1 BMS Functionality  BMS 功能
The BMS system of eBlock-100C energy block adopts battery and converter collaborative control technology.
Each battery module management unit BMU collects the voltage, temperature of the battery cells inside the battery pack and communicates with the BCS (Battery&Converter Collaborative Control Unit).
BCS combines other collected data (including environmental temperature, cabinet temperature, battery status, and other series of parameters) with scheduling instructions to take balancing measures on the battery and control the charging and discharging power of the converter PCS.
eBlock-100C能量块的BMS系统采用电池&变流器协同控制技术。
每个电池模块管理单元BMU采集电池Pack内电芯电压、温度至BCS（电池&变流器协同控制单元）。
BCS结合采集的其他数据（包括环境温度、柜内温度、电池状态等系列参数）以及调度指令，对电池采取均衡措施以及对变流器PCS充放电进行功率控制。

BMS can be integrated with PCS for design, greatly reducing the possibility of protection unit action timing, action delay, and local fault protection failure within the energy storage system, and designing graded actions and linkage mechanisms for protection.
BMS与PCS融合设计，大幅减少储能系统内保护单元动作时序、动作延时以及局部故障保护失效的可能性，设计保护的分级动作和联动机制。

4.4 Power Conversion System 储能变流器
4.4.1 Topology Diagram 拓扑图

[image: image5.emf]PV1+

PV2+

PV1-

PV2-

PV3+

PV4+

PV3-

PV4-

PV5+

PV6+

PV5-

PV6-

PV7+

PV8+

PV7-

PV8-

Breaker

EMI MPPT

EMI

Contactor

BAT+

BAT-

DC/AC

DCDC

Filter

GFCI Relay

EMI Relay

EMI Relay

A

B

C

N

A

B

C

N

GRID

Backup

Control Unit

Auxiliary power supply

Surge 

Protector

Surge 

Protector


Topology diagram of PCS
PCS的拓扑图

The Power Conversion System (PCS) can automatically track the maximum power point of the connected photovoltaic panels to maximize power generation. It can also accept the energy dispatching from the Energy Management System (EMS). When the system is unable to absorb the power from the photovoltaic panels, it will promptly limit the power output.The PCS can charge and discharge the batteries according to the instructions from the Battery Management System (BMS) and the EMS, and ensure the reliable operation of the batteries based on comprehensive factors such as the State of Charge (SOC).

PCS可以自动追踪接入光伏板的最大功率点，以使发电量最大，并可以接受EMS的能量调度，当系统消纳不了光伏的功率时，及时限制功率输出；PCS可以根据BMS及EMS的指令进行电池的充放电，根据SOC状态等综合因素保证电池的可靠运行；

The PCS provides two alternating current (AC) ports. One is the grid-connected interface, and the other is the off-grid interface. The grid-connected interface can automatically track the frequency and phase of the power grid for grid-connected operation and provide supplementary power support for the system according to the EMS. The off-grid interface can supply a stable power source for customer loads.

PCS提供两个交流端口，一个为并网接口，一个为离网接口，并网接口可自动跟踪电网频率相位进行并网运行，根据EMS以及法规的要求进行有功及无功的功率输出，离网接口可为客户负载提供稳定的电源；

Moreover, the PCS has a reliable power supply guarantee. When the PCS malfunctions, it can bypass the output in a timely manner. Or when the power grid fails, it can quickly enter the pure off-grid operation state to ensure the safety of power usage.

且PCS有着可靠的用电保证，当PCS出现故障时，可及时旁路输出，或电网掉电后，迅速进入纯离网运行状态，保证用电安全。
4.4.2 Product Specification 产品规格

Technical Parameters of PCS
PCS技术参数

	Type Designation
类型名称
	JS050FA

	光伏输入参数PV Input Data

	最大光伏输入功率
Maximum Photovoltaic Input Power
	100kWp

	最大直流输入电压
Maximum DC Input Voltage
	1000V

	额定直流输入电压
Rated DC Input Voltage
	720V

	启动电压Starting Voltage
	180V

	MPPT电压范围
MPPT Voltage Range
	150-900V

	MPPT数量Group
	4

	每路MPPT输入组数
Number of MPPT Input Groups per Route
	2

	每路MPPT最大输入电流
Maximum Input Current of Each MPPT
	40A

	电池输入参数Battery Input Data

	电池电压范围(V)

Battery Voltage Range (V)
	358.4~460.8V

	最大充电/放电电流(A)
Maximum Charging /Discharge Current (A)
	139.5A

	最大充放电功率(kW)
Maximum Charge and Discharge Power (kW)
	50kW

	交流输入输出参数（电网侧）AC Input/Output Data (Grid side)

	额定输出功率
Rated Output Power
	50kW

	最大输出视在功率
Maximum Output Apparent Power
	55kVA

	交流额定输出电流
AC Rated Output Current
	72.2A

	功率因数
Power Factor
	-0.8~0.8

	电网电压
Grid Voltage
	3L/N/PE 230/400V

	电网频率
Grid Frequency
	50Hz

	电网最大输入电流
Maximum Input Current of the Power Grid
	144A

	离网侧参数（离网模式）Backup Data (Off-grid mode)

	额定输出功率
Rated Output Power
	50kW

	离网峰值功率/长时
Off-grid Peak Power/Long time
	55kVA

	离网峰值功率/1分钟
Off-grid Peak Power /1 min
	60kVA

	最快并离网切换时间
Fastest on/off Grid Switching Time
	＜10ms

	功率因数
Power Factor
	-0.8~0.8

	额定输出电压
Rated Output Voltage
	3L/N/PE 400V

	电压频率
Voltage Frequency
	50Hz

	混合逆变器系统参数Hybrid Converter System Data

	工作温度范围
Operating Temperature Range
	-35~60℃(>45℃降额)(>45℃ derate)

	冷却方式Cooling Mode
	液冷Liquid Cooling

	湿度Humidity
	0~95%

	防护等级 Protection Level
	IP65


4.5 Auxiliary Equipment 辅助设备
4.5.1 Liquid Cooling System 液冷系统
The system uses a liquid cooling system for heat dissipation. 

Liquid cooling is a technology that uses liquid as a refrigerant to remove heat from cells. It has excellent temperature homogeneity and low power consumption. The liquid cooling system mainly consists of pipes, pumps, heat ex-changer  and compressors. The coolant of the system is ethylene glycol liquid. 

系统采用液冷散热方式。
液冷是一种利用液体作为制冷剂，从电池中去除热量的技术。它具有优异的温度均匀性和低功耗。液冷系统主要由管道、泵、热交换器和压缩机组成。该系统的冷却剂为乙二醇水溶液。
4.5.2Fire Suppression System  消防系统
1 Fire protection system scheme消防系统方案

eBlock-100C产品消防方案为簇级消防气溶胶、簇级水消防、簇级复合型探测器。具体消防说明可参考用户手册。
eBlock-100C product fire protection solutions are rack level fire aerosol, rack level water fire protection, rack level composite detector.For details about the fire protection system scheme, see the user manual.

储能消防联动系统可分为消防探测系统、消防灭火系统及应急水喷淋，当发生火情时，消防灭火系统迅速介入，进行探测、报警、灭火等动作；若火情蔓延或发生复燃现象，消防灭火系统无法控制火情时，可接入应急水喷淋进行紧急处置，防止发生爆燃、火灾等严重后果。

The energy storage fire linkage system can be divided into fire detection system, fire extinguishing system and emergency water spray. When a fire occurs, the fire extinguishing system quickly intervenes to detect, alarm and extinguish the fire. If the fire spreads or refires occur, and the fire extinguishing system cannot control the fire, emergency water spray can be connected for emergency disposal to prevent deflagration, fire and other serious consequences.

5.Technical Documents and Drawings技术文件和图纸
5.1.General Requirements一般要求
Documentation should be well-organized with a strong logical structure. The content of the documentation must be correct, accurate, consistent, clear, and complete, meeting the engineering requirements.

文件结构清晰、逻辑性强。文件内容正确、准确、一致、清晰完整，满足工程要求。
5.2. Required Technical Documents and Drawings 要求的文件及图纸

Scope list of documents
文件范围清单
	No.
	Document name文件名称
	Specification规格
	Delivery Schedule交货时间表

	1
	Equipment Layout Drawing

设备布置图
	Electronic files

电子文件
	Provided before the Product arrival a site在产品到达现场之前提供

	2
	Foundation Drawing

基础图
	Electronic files

电子文件
	Provided before the Product arrival a site在产品到达现场之前提供

	3
	Factory Testing

工厂测试报告
	Electronic files

电子文件
	Provided together with the Product
与产品一起提供


5.3.Documents and Drawings to be Provided with the Shipment随运提供的文件和图纸

Scope list of documents
文件范围清单
	No.
	Document name文件名称
	Specification规格
	Delivery Schedule交货时间表

	1
	User Manual
用户手册
	Paper files Or Electronic files纸质文件或电子文件
	Provided together with the Product
与产品一起提供

	2
	Equipment List
设备清单
	Paper files Or Electronic files纸质文件或电子文件
	Provided together with the Product
与产品一起提供

	3
	Installation Manual
安装手册
	Paper files Or Electronic files纸质文件或电子文件
	Provided together with the Product
与产品一起提供

	4
	Type Test Report
型式试验报告
	Paper files Or Electronic files纸质文件或电子文件
	Provided together with the Product
与产品一起提供

	5
	Manufacturer's Warranty Card
制造商的保修卡
	Paper files Or Electronic files纸质文件或电子文件
	Provided together with the Product
与产品一起提供


6.Miscellaneous其它事项
1) This Agreement shall enter into force on the date on which it is signed and sealed by both parties. upon the signature by both parties.

本协议自双方签字盖章之日起生效。
2) The provision of confidentiality requirement sand intellectual property rights as  set forth in the Main Contract or non-disclosure agreement shall apply to this  Agreement.

主合同或保密协议中规定的保密要求和知识产权适用于本协议。
3)This Agreement is an integral part of the Main Contract.Any matter that is not  covered herein shall be subject to the Main Contract.In the event of any conflict  between the Main Contract and this Agreement,  this Agreement shall prevail.

本协议是主合同不可分割的组成部分。本合同未尽事宜以主合同为准。如果主合同与本协议有任何冲突，以本合同为准。 

.........................(Buyer Company Name买方公司名称) 

Signature签名:            

Name名字:           

.........................(Seller Company Name卖方公司名称) 

Signature签名:            

Name名字:           

[image: image9.png]
[image: image10.png]

PV1+
PV2+
PV1-
PV2-
PV3+
PV4+
PV3-
PV4-
PV5+
PV6+
PV5-
PV6-
PV7+
PV8+
PV7-
PV8-

Breaker
EMI
MPPT

EMI
Contactor
BAT+
BAT-
DC/AC
DCDC
Filter
GFCI
Relay
EMI
Relay
EMI
Relay
A
B
C
N
A
B
C
N
GRID
Backup
Control Unit
Auxiliary power supply
Surge Protector
Surge Protector




